Cooling Tower & Condenser Water Systems, Thermostatic Mixing Valves & Water Features

Test:	 Legionella pneumophila serogroup 1-14 count, Legionella species count and Total Legionella Count with Heterotrophic Plate Count (HPC)

Standard:	Australian Standards AS/NZS 3896:2017 & AS 4276.3.2:2003; AS4276.3.1: 2007

Status:	This testing is accredited with NATA

Procedure:

- Experienced and trained IMC staff will collect all water samples from each system nominated in properly pre sterilised bottles using validated sampling procedures.

- IMC will transfer samples to the motor vehicle in an insulated cooler bag containing an ice brick, and then transfer all samples into an insulated motor vehicle refrigerator for transportation to our laboratory.

- IMC will attach an IMC adhesive tag to each water system to enable easy identification of those systems so that there is no confusion as to where the samples were collected.

- All samples will be delivered to our laboratory as per the standard within 24hrs for Legionella Bacterium and Heterotrophic Plate Count (HPC) and testing commenced immediately on receipt at the laboratory.

Frequency:	Legionella and Heterotrophic Plate Count (HPC) testing should be performed on a MONTHLY basis so that you can monitor the level of Legionella in each system and so that you can assess the biological cleanliness using Heterotrophic Plate Count (HPC).

Interpretation:

- Legionella counts of 1000 colony forming units (cfu) per mL or higher are considered serious and have been associated with outbreaks and in the deaths of people. The relevant Australian standards and guidelines require that there be no detection of Legionella Bacterium.

- Heterotrophic Plate Count (HPC) has no relationship in the detection of Legionella. HPC are used to measure the level of water cleanliness. HPC counts equal to or greater than 100,000 cfu/mL, are not recommended and usually indicate poor biological control. The higher the count the worse is the control.

Reporting:

- The testing of waters for Legionella Bacterium takes a minimum of 7 days and a maximum 10 days.

- Testing of waters for HPC is 2 days. Where a sample is collected for both tests and no request is made to split that sample, we will report both results on a single report.

- To receive a result for HPC earlier than the full report time you must advise IMC prior to our collection of the sample.

- High counts for both Legionella and HPC will be telephoned to the nominated person at your facility once results are released from the laboratory. All other results that are within the recommended guidelines will be emailed to the nominated recipients as Private, & Confidential. IMC do not send hard copies by mail.

Corrosion Coupon Monitoring for Cooling Water Systems

Test:	The measuring of corrosion levels in cooling water systems is considered to be a valuable tool in assessing the overall performance of a chemical supplier and their ability to maintain acceptable corrosion rates in line with appropriate guidelines. The time of exposure for corrosion coupons must be considered in the evaluation of results. However, meaningful results of practical value can only be obtained by the use of equipment compliant with the industry standard (ASTM D2688-15) and operated by the guidelines contained therein. This quotation is for the supply of ASTM compliant corrosion coupons and processing of one mild steel and one copper corrosion coupon per quarter per system.
It is recommended that the water flow rate through the racks of each system be calibrated ultrasonically. ASTM D2688 specifies an acceptable water flow rate range to ensure that soft metal erosion (on metals such as copper and its alloys) is not confused with and interpreted as corrosion. Flow rate should be routinely checked ultrasonically every six months, and after major plant operational disruptions.

Standard:	ASTM Standard D2688-15; G1-3.

Procedure:	IMC will: -

- Supply the corrosion coupons and install them in the corrosion rig. The site occupier has a responsibility to provide safe access/egress to building sites.

- At the end of approximately 90 days, return to collect those coupons, remove, and replace the old coupons with new coupons, take the removed coupons to our laboratory for cleaning, weighing, and reporting.

Frequency:	The monitoring of corrosion levels should be performed on a Quarterly basis approx. every 90 days).

Reporting:

- A report will be prepared based on the information gained advising of the rates of corrosion for both Mild Steel & Copper coupons. The report includes a digital photograph of the coupons before they have been cleaned and after they have been cleaned and weighed. Coupons can be returned to you for your inspection if so wished, otherwise they will be disposed of.

The report will be emailed to the nominated recipients as Private, & Confidential. IMC do not send hard copies by mail.

*Please note corrosion coupons will be invoiced for the whole year at the start of contract*

FOR THE SUPPLY OF ONE, ASTM STANDARD D2688-15; G1-3 COMPLIANT 4 PROBE CORROSION RACK

INSTALLATION AND FREIGHT (IF NECCESARY) IS ADDITIONAL TO THE CHARGES SHOWN

Cooling Tower, Condenser Water Systems & Pool/Spas Microbial Trending

Procedure:

- Written authority must be provided to authorise the release of each report on a monthly basis to IMC.

- IMC will trend all microbial results against the regulatory standards/guidelines.

- IMC will issue an ongoing microbial trend on a monthly basis.

Frequency:	Legionella and Heterotrophic Plate Count (HPC) trend will be performed on a MONTHLY basis so that you can monitor the level of Legionella in each system and so that you can assess the biological cleanliness using Heterotrophic Plate Count (HPC).

Corrosion trends of Mild Steel and Copper and Stainless Steel where required will be performed on a QUARTERLY basis to monitor the level of corrosion within each system.

Interpretation:

- Legionella counts of 1000 colony forming units (cfu) per mL or higher are considered serious and have been associated with outbreaks and in the deaths of people. The relevant Australian standards and guidelines require that there be no detection of Legionella Bacterium.

- Heterotrophic Plate Count (HPC) has no relationship in the detection of Legionella. HPC are used to measure the level of water cleanliness. HPC counts equal to or greater than 100,000 cfu/mL, are not recommended and usually indicate poor biological control. The higher the count the worse is the control.

- Mild Steel corrosion rates should be <0.15mpy

- Copper corrosion rates should be <0.0125mpy

Reporting:

- A copy of each trend will be provided following the receipt of the final reports released from their respective laboratories.

- All results are recorded on an ongoing trend with the acceptable levels underneath a highlighted red line.

- All reports will be emailed to the nominated recipients. IMC do not send hard copies by mail.

Risk Management Plans (Risk Assessment) of Cooling Water Systems

Test:	The Risk Management Plan is a document outlining measures put in place/and to put in place to manage the risk of the public/staff being exposed to Legionella in a cooling system.

Standard:	Victoria:  Public Health and Wellbeing Act 2008, NSW: Department of Health Guidelines NSW Public Health (Microbial Control) Regulation 2012, Clause 8, 9, 10 & 11 and AS/NZS 3666.2:2002 & AS/NZS 3666.3:2000, QLD: Workplace Health and Safety Queensland, Guide to Legionella Control in Cooling Water Systems, including Cooling Towers V2.06-08 Guidelines

Procedure:	IMC will: -

- Conduct a site review to examine operational procedures currently in place including a review of relevant records and reports. It also includes site specific characteristics.

- Opportunities and considerations to reduce detected risks are proposed in the plan. Conduct a comprehensive inspection of onsite equipment and all records.

- Produce a report complete with recommendations.

Frequency:	Victoria: 12 monthly, Other states: Recommend 12 monthly

Reporting:

- A report will be prepared based on the information gained. Including

- Critical risks: Stagnant water, Nutrient growth, Poor water quality, Deficiencies in Cooling tower, Location and Access.

The report will be sent electronically as Private, & Confidential

Corrosion Rack Flow Rate Calibration

Overview:

The flow rate through corrosion rack is calibrated to ensure testing is compliant to ASTM D2688-15, producing accurate and reliable corrosion rates for the system.

ASTM D2688-15 stipulates that the flow rate through the corrosion coupon rack should be set between 0.4 and 1.8 m/sec.

Calibration of Corrosion Coupon Rack

The portable Ultrasonic Flow Meter (UFM) measures the flow velocity and volume of liquids within a pipe. It is a Non-Destructive Test (NDT) and is a safe non-intrusive process requiring ultrasonic transducers to be temporarily clamped onto the outside of the pipe. The unit measures the impact of the water flow rate on the behaviour of the sound waves which is then translated automatically into linear velocity data.

The water flow rate through the corrosion coupon rack will then be assessed and adjusted to ensure the flow rate through the corrosion rack meets the requirements of ASTM standard D2688-15

Note - Calibration checks should be done at a minimum of every 12 months or after any changes to the water treatment equipment to ensure the flow rate through the corrosion rack conforms to the ASTM standard.

Standard:	ASTM Standard D2688-15

Frequency:	6 monthly

Objectives:

The flow rate through the corrosion coupon rack is determined using an ultrasonic flow rate meter.

Using the flow control valve, the flow rate is calibrated to conform to ASTM D2688-15.

Procedures:

AWT will visit site as required to perform the various services as per the Scope of Works.

Mandatory completion of all Job Safety Assessment and Safe Work Method statements for all work performed.

Reporting:	A confirmation of the calibrated flow rate through the corrosion rack will be supplied in the form of a calibration certificate and emailed to the nominated site contact

Testing of Swimming Pools and Spas

Test:	Escherichia coli, Standard Plate Count, Pseudomonas spp and Legionella

Standard:	AS4276.7:2007, AS4276.3.1: 2007, AS4276.13:2008, AS/NZS 3896:2008 in line with the Dept. of Health NSW Australia	Guidelines for Public Swimming Pools & Public Spa Pools – June 1996.

Status:	Microbiological testing is accredited with NATA

Procedure:

- Experienced and trained IMC staff will collect all water samples from each system nominated in properly pre sterilised bottles using validated sampling procedures The site occupier has a responsibility to provide safe access/egress to building sites.

- IMC will transfer samples to the motor vehicle in an insulated cooler bag containing an ice brick, and then transfer all samples into an insulated motor vehicle refrigerator for transportation to our laboratory.

- IMC will attach an IMC adhesive tag to each water system to enable easy identification of those systems so that there is no confusion as to where the samples were collected.

- All samples will be delivered to our laboratory within 24hrs for testing & commenced immediately on receipt at the laboratory.

Frequency:	The testing of the Swimming Pool Water for chemical levels should be performed daily by the operator.

The microbiological testing should be performed on a MONTHLY basis, as per the quoted guideline, so that you can monitor the level of bacteria and assess the biological cleanliness.

Interpretation:

- SPC counts above <100 cfu/mL, are unacceptable.

- E.coli counts should not be detected

- Pseudomonas spp should not be detected in 100 mL.

Reporting:

- The microbiological testing of Swimming Pool waters for the nominated Bacterium takes a maximum 4 days.

- High counts for both Legionella and HPC will be telephoned to the nominated person at your facility once results are released from the laboratory. All other results that are within the recommended guidelines will be emailed to the nominated recipients as Private, & Confidential. IMC do not send hard copies by mail.

- The chemical testing for these parameters will be performed on the day received at the laboratory and results are available within 24hours.

Testing of Potable Water/Ice

Test:	Coliforms and Escherichia coli (E.coli)

Standard:	AS 4276.5:2007

AS 4276.7:2007

Status:	Microbiological testing is accredited with NATA

Procedure:

- Experienced and trained IMC staff will collect all water samples from each system nominated in properly pre sterilised bottles using validated sampling procedures.

- IMC will transfer samples to the motor vehicle in an insulated cooler bag containing an ice brick, and then transfer all samples into an insulated motor vehicle refrigerator for transportation to our laboratory.

- IMC will attach an IMC adhesive tag to each water system to enable easy identification of those systems so that there is no confusion as to where the samples were collected.

- All samples will be delivered to our laboratory within 24hrs for testing & commenced immediately on receipt at the laboratory.

Frequency:	The testing of AQIS Water for microbiological testing should be performed on a MONTHLY basis so that you can monitor the level of bacteria and assess the biological cleanliness.

Interpretation:

- Coliform counts should not be detected.

- E.coli  should not be detected

Reporting:

- The microbiological testing of waters for the nominated Bacterium takes between 2 and 5 days.

- High counts for both Legionella and HPC will be telephoned to the nominated person at your facility once results are released from the laboratory. All other results that are within the recommended guidelines will be emailed to the nominated recipients as Private, & Confidential. IMC do not send hard copies by mail.

Indoor Air Quality monitoring for air contaminants in an office space:

We have pleasure in submitting the proposal to conduct Indoor Air Quality (IAQ) monitoring of air contaminants in an office space. IMC is an independent, professional, quality driven microbiological and environmental sampling, testing, and consulting service operating throughout Australia, Malaysia, Thailand and Asia specialising in water, indoor air quality, hygiene and food.

The proposal is based on the below standard to conduct Indoor Environmental Air Quality monitoring.

Test:

Standard IAQ Testing – CO, CO2, Relative Humidity, Temperature, Dust (PM10) and Total Volatile Organic Compounds (TVOCs)

Standard:

- ANSI/ASHRAE 62.1-2016: Ventilation for Acceptable Indoor Air Quality.

- AS 1668.2-2002: The use of ventilation and air-conditioning in the buildings

- Safe Work Australia: Managing the Work environment and Facilities.

Equipment and Procedure:

- A portable direct reading instrument (3M™ EVM7) is used to measure the Indoor Environmental Quality (IEQ) parameters such as Temperature, Relative humidity, Carbon dioxide and Carbon monoxide. Handheld aerosol monitor 3M™ EVM7 is used to measure the Respirable suspended Particulate Matter (PM10) in the atmosphere.

- A portable direct reading instrument will be used to measure Total Volatile Organic Compounds (TVOCs) present within the office space.

- The total number of samples and the location will be decided mutually by facilities management and IMC Environs.

- A detailed Assessment report will be submitted to the client within maximum of 30 working days from the date of monitoring.

Frequency:

The testing of Indoor Air Quality for physical parameter levels should be performed on a Yearly basis to monitor the indoor air quality compared to the outside air.

Reporting:

Report is written in a laboratory report format, including result data, tables, figures and simple result discussion.